POLYETHYLENE TANK PACKAGE:

- The chemical feed tank shall be (30,55,100) gallons and shall be transparent polyethylene so the liquid level is visible at all times.  The tank shall be furnished with a steel stand and removable lid.

- The chemical feed package shall include the following items for a complete package:

  - Pump section piping including a shut-off valve and strainer.

  - Angle mount agitator with carbon shaft and 4” prop specially made to fit the tank depth.  The agitator motor shall be ¼ HP, 120/1/60, and a totally enclosed non-ventilated enclosure (TENV).

    - A piston style pump shall also be mounted and piped at the factory for a turn-key package and be rated for a 1000 PSI maximum output.  The pump shall be capable of (1,8,3,6) GPH with a minimum recommended output adjustment of 20% of maximum.  The pump shall have the following additional features:

      - (5/8)” diameter piston

      - Carbon steel wet end

      - 56C flange mount drive

      - ¼ HP, 120/1/60 motor

      - Totally Enclosed Fan Cooled (TEFC) motor

# CARBON STEEL TANK PACKAGE:

- The chemical feed tank shall be (50,100) gallons and shall be made of 10 gauge carbon steel with a brass sight glass valve assembly so the liquid level is visible at all times.  The tank shall be furnished with a steel stand and hinged lid.

- The chemical feed package shall include the following items for a complete package:

  - Carbon steel pump suction piping including a shut-off valve and cast iron strainer.

  - Angle mount agitator with carbon shaft and 4” prop specially made to fit the tank depth.  The agitator shall be ¼ HP, 120/1/60, and a totally enclosed non-ventilated enclosure (TENV).

    - A piston style pump shall also be mounted and piped at the factory for a turn-key package and be rated for a 1000 PSI maximum output.  The pump shall be capable of (1,8,3,6) GPH with a minimum recommended output adjustment of 20% of maximum.  The pump shall have the following additional features:

      - (5/8)” diameter piston

      - Carbon steel wet end

      - 56C flange mount drive

      - ¼ HP, 120/1/60 motor

      - Totally Enclosed Fan Cooled (TEFC) motor

# 304 STAINLESS STEEL TANK PACKAGE:

- The chemical feed tank shall be (50,100) gallons and shall be made of 10 gauge 304 stainless steel with a stainless sight glass valve assembly so the liquid level is visible at all times.  The tank shall be furnished with a steel stand and hinged lid.

- The chemical feed package shall include the following items for a complete package:

  - Stainless steel pump suction piping including a shut-off valve and stainless strainer.

  - Angle mount agitator with a 304 stainless shaft and 4” prop specially made to fit the tank depth.  The agitator motor shall be ¼ HP, 120/1/60, and a totally enclosed non-ventilated enclosure (TENV).

    - A piston style pump shall also be mounted and piped at the factory for a turn-key package and be rated for a 1000 PSI maximum output.  The pump shall be capable of (1,8,3,6) GPH with a minimum recommended output adjustment of 20% of maximum.  The pump shall have the following additional features:

      - 5/8)” diameter piston

      - 303 stainless steel wet end

      - 56C flange mount drive

      - ¼ HP, 120/1/60 motor

      - Totally Enclosed Fan Cooled (TEFC) motor

OPTIONS AVAILABLE FOR ALL CHEMICAL FEED PACKAGES

- Stainless steel options (all stainless steel tanks have the following stainless steel options as standard):

  - 316SS piping for each pump

  - 316SS sight glass valve assembly for carbon steel tank instead of brass

  - 304SS shaft and 4” prop for agitator

    - Diaphragm pumps in place of piston pumps:

      - 5/8” diameter stainless piston

      - Teflon diaphragm

      - 56C flange mount drive

      - (1.8,3,6) GPH availability

      - Polyethylene wet end (100 PSI max output) or 303 stainless steel wet end (800 PSI max output)

      - ¼ HP, 120/1/60, TEFC motor

        - Electrical package that includes Nema 12 panel, mixer on/off switch, HOA switch per pump, power relay for motors, fuses, and terminal strip.  Low water alarm with controller can be added as an option.

        - Two pumps can be mounted on a single tank.