## DEAERATOR SIZING PROGRAM
Bryan Steam Deaerator Sizing Program | [5 empty] | Steam Table
highlighted cells are for job conditions |  |  |  | revision date: 9/17/02 |  |  |  | Specific Volume |  | Enthalpy |  |  | Entropy |  |  | Internal Energy
and to be entered by user | [6 empty] | Fahr.
[6 empty] | Abs. press. Lb/sq. in. | Temp. | Sat. Liquid | Sat. Vapor | Sat. Liquid | Evap. | Sat. Vapor | Sat. Liquid | Evap. | Sat. Vapor | Sat. Liquid | Evap. | Sat. Vapor
Capacity | 70000 | PPH |  |  |  | 14.696 | 212 | 0.01672 | 26.8 | 180.07 | 970.3 | 1150.37 | 0.312 | 1.4446 | 1.7566 | 180.02 | 897.48 | 1077.5
Steam pressure to the PRV | 5 | PSI |  |  |  | 15 | 213.03 | 0.01672 | 26.29 | 181.11 | 969.7 | 1150.81 | 0.3135 | 1.4415 | 1.755 | 181.06 | 896.74 | 1077.8
Saturated steam temperature at bop | 227.96 | Degrees |  |  |  | 16 | 216.32 | 0.01674 | 24.75 | 184.42 | 967.6 | 1152.02 | 0.3184 | 1.4313 | 1.7497 | 184.37 | 894.33 | 1078.7
Deaerator operating pressure | 5 | PSI |  |  | 227.96 | 17 | 219.44 | 0.01677 | 23.39 | 187.56 | 965.5 | 1153.06 | 0.3231 | 1.4218 | 1.7449 | 187.51 | 891.99 | 1079.5
Saturated temp. at deaerator pressure | 227.96 | Degrees |  |  |  | 18 | 222.41 | 0.01679 | 22.17 | 190.56 | 963.6 | 1154.16 | 0.3275 | 1.4128 | 1.7403 | 190.5 | 889.9 | 1080.4
Enthalpy of Steam | 960.1 | BTU's/ LB |  |  | 227.96 | 19 | 225.24 | 0.01681 | 21.08 | 193.42 | 961.9 | 1155.32 | 0.3317 | 1.4043 | 1.736 | 193.36 | 887.84 | 1081.2
Percentage of incoming Water | 100% |  |  |  |  | 20 | 227.96 | 0.01683 | 20.089 | 196.16 | 960.1 | 1156.26 | 0.3356 | 1.3962 | 1.7318 | 196.1 | 885.8 | 1081.9
Temperature of incoming Water | 40 | Degrees |  |  |  | 21 | 230.57 | 0.01685 | 19.192 | 198.79 | 958.4 | 1157.19 | 0.3395 | 1.3885 | 1.728 | 198.73 | 883.87 | 1082.6
Pressure of incoming Water | 40 | PSI |  |  |  | 22 | 233.07 | 0.01687 | 18.375 | 201.33 | 956.8 | 1158.13 | 0.3431 | 1.3811 | 1.7242 | 201.26 | 882.04 | 1083.3
Percentage of Condensate Return | 0% |  |  |  |  | 23 | 235.49 | 0.01689 | 17.627 | 203.78 | 955.2 | 1158.98 | 0.3466 | 1.374 | 1.7206 | 203.71 | 880.19 | 1083.9
Temperature of Condensate Return | 10 | Degrees |  |  |  | 24 | 237.82 | 0.01691 | 16.938 | 206.14 | 953.7 | 1159.84 | 0.35 | 1.3672 | 1.7172 | 206.07 | 878.53 | 1084.6
Percentage of liquid from 5% steam | 0.01683 |  |  |  |  | 25 | 240.07 | 0.01692 | 16.303 | 208.42 | 952.1 | 1160.52 | 0.3533 | 1.3606 | 1.7139 | 208.34 | 876.76 | 1085.1
| 1.0168 |  |  |  |  | 26 | 242.25 | 0.01694 | 15.715 | 210.62 | 950.7 | 1161.32 | 0.3564 | 1.3544 | 1.7108 | 210.54 | 875.16 | 1085.7
[6 empty] | 27 | 244.36 | 0.01696 | 15.17 | 212.75 | 949.3 | 1162.05 | 0.3594 | 1.3484 | 1.7078 | 212.67 | 873.63 | 1086.3
INT STEAM REQUIRED | 13703.9892 |  |  |  |  | 28 | 246.41 | 0.01698 | 14.663 | 214.83 | 947.9 | 1162.73 | 0.3623 | 1.3425 | 1.7048 | 214.74 | 872.06 | 1086.8
MAKE-UP WATER REQUIRED | 58539.6234 | 70000 | MR |  |  | 29 | 248.4 | 0.01699 | 14.189 | 216.86 | 946.5 | 1163.36 | 0.3652 | 1.3368 | 1.702 | 216.77 | 870.53 | 1087.3
CONDENSATE RETURN REQUIRED | 0 | 0 | CR |  |  | 30 | 250 | 0.01701 | 13.746 | 218.82 | 945.3 | 1164.12 | 0.368 | 1.3313 | 1.6993 | 218.73 | 869.07 | 1087.8
STEAM REQUIRED | 11460.3766 | 11460.3766 | SR |  | 0.80423 | 31 | 252.22 | 0.01702 | 13.33 | 220.73 | 944 | 1164.73 | 0.3707 | 1.326 | 1.6967 | 220.63 | 867.67 | 1088.3
| 70000 | 81460.3766 |  |  | 0.19577 | 32 | 254.05 | 0.01704 | 12.94 | 222.59 | 942.8 | 1165.39 | 0.3733 | 1.3209 | 1.6942 | 222.49 | 866.21 | 1088.7
[6 empty] | 33 | 255.84 | 0.01705 | 12.572 | 224.41 | 941.6 | 1166.01 | 0.3758 | 1.3159 | 1.6917 | 224.31 | 864.89 | 1089.2
Water line information | [5 empty] | 34 | 257.58 | 0.01707 | 12.226 | 226.18 | 940.3 | 1166.48 | 0.3783 | 1.311 | 1.6893 | 226.07 | 863.53 | 1089.6
Make-up water GPM required | 117.0207 | GPM |  |  | 1.9503 | 35 | 259.28 | 0.01708 | 11.898 | 227.91 | 939.2 | 1167.11 | 0.3807 | 1.3063 | 1.687 | 227.8 | 862.3 | 1090.1
Incoming line Size (min.size) | 3.5 | based on 4ft per second |  |  |  | 36 | 260.95 | 0.01709 | 11.588 | 229.6 | 938 | 1167.6 | 0.3831 | 1.3017 | 1.6848 | 229.49 | 861.01 | 1090.5
[6 empty] | 37 | 262.57 | 0.01711 | 11.294 | 231.26 | 936.9 | 1168.16 | 0.3854 | 1.2972 | 1.6826 | 231.14 | 859.76 | 1090.9
CV factor for water valve is | 23.76 |  |  |  |  | 38 | 264.16 | 0.01712 | 11.015 | 232.89 | 935.8 | 1168.69 | 0.3876 | 1.2929 | 1.6805 | 232.77 | 858.53 | 1091.3
[6 empty] | 39 | 265.72 | 0.01714 | 10.75 | 234.48 | 934.7 | 1169.18 | 0.3898 | 1.2886 | 1.6784 | 234.36 | 857.24 | 1091.6
[6 empty] | 40 | 267.25 | 0.01715 | 10.498 | 236.03 | 933.7 | 1169.73 | 0.3919 | 1.2844 | 1.6763 | 235.9 | 856.1 | 1092
[6 empty] | 41 | 268.74 | 0.01716 | 10.258 | 237.55 | 932.6 | 1170.15 | 0.394 | 1.2803 | 1.6743 | 237.42 | 854.98 | 1092.4
[6 empty] | 42 | 270.21 | 0.01717 | 10.029 | 239.04 | 931.6 | 1170.64 | 0.396 | 1.2764 | 1.6724 | 238.91 | 853.79 | 1092.7
Specific volume of 5 PSIG steam | 20.089 |  |  |  |  | 43 | 271.64 | 0.01719 | 9.81 | 240.51 | 930.6 | 1171.11 | 0.398 | 1.2726 | 1.6706 | 240.37 | 852.73 | 1093.1
Specific volume of income PSIG steam | 21.08 |  |  |  | 21.08 | 44 | 273.05 | 0.0172 | 9.601 | 241.95 | 929.6 | 1171.55 | 0.4 | 1.2687 | 1.6687 | 241.81 | 851.59 | 1093.4
[6 empty] | 45 | 274.44 | 0.01721 | 9.401 | 243.36 | 928.6 | 1171.96 | 0.4019 | 1.265 | 1.6669 | 243.22 | 850.48 | 1093.7
| 7000 |  |  |  |  | 46 | 275.8 | 0.01722 | 9.209 | 244.75 | 927.7 | 1172.45 | 0.4038 | 1.2613 | 1.6651 | 244.6 | 849.5 | 1094.1
Steam line Information | [5 empty] | 47 | 277.13 | 0.01723 | 9.025 | 246.12 | 926.7 | 1172.82 | 0.4057 | 1.2577 | 1.6634 | 245.97 | 848.43 | 1094.4
Steam required in PPH | 12606.4143 |  |  |  |  | 48 | 278.45 | 0.01725 | 8.848 | 247.47 | 925.8 | 1173.27 | 0.4075 | 1.2542 | 1.6617 | 247.32 | 847.38 | 1094.7
[6 empty] | 49 | 279.74 | 0.01726 | 8.678 | 248.79 | 924.9 | 1173.69 | 0.4093 | 1.2508 | 1.6601 | 248.63 | 846.37 | 1095
[6 empty] | 50 | 280.81 | 0.01727 | 8.515 | 250.09 | 924 | 1174.09 | 0.411 | 1.2474 | 1.6584 | 249.93 | 845.37 | 1095.3
Income line size (min. size) | 10 | based on 7000 ft per minute |  |  |  | 51 | 282.26 | 0.01728 | 8.359 | 251.37 | 923 | 1174.37 | 0.4127 | 1.2442 | 1.6569 | 251.21 | -251.21
Connection to Deaerator (min. size) | 10 |  |  |  |  | 52 | 283.49 | 0.01729 | 8.208 | 252.63 | 922.2 | 1174.83 | 0.4144 | 1.2409 | 1.6553 | 252.46 | -252.46
[6 empty] | 53 | 284.7 | 0.0173 | 8.062 | 253.87 | 921.3 | 1175.17 | 0.4161 | 1.2377 | 1.6538 | 253.7 | -253.7
[6 empty] | 54 | 285.9 | 0.01731 | 7.922 | 255.09 | 920.5 | 1175.59 | 0.4177 | 1.2346 | 1.6523 | 254.92 | -254.92
[6 empty] | 55 | 287.07 | 0.01732 | 7.787 | 256.3 | 919.6 | 1175.9 | 0.4193 | 1.2316 | 1.6509 | 256.12 | -256.12
[6 empty] | 56 | 288.23 | 0.01733 | 7.656 | 257.5 | 918.8 | 1176.3 | 0.4209 | 1.2285 | 1.6494 | 257.32 | -257.32
[6 empty] | 57 | 289.37 | 0.01734 | 7.529 | 258.67 | 917.9 | 1176.57 | 0.4225 | 1.2255 | 1.648 | 258.49 | -258.49
[6 empty] | 58 | 290.5 | 0.01736 | 7.407 | 259.82 | 917.1 | 1176.92 | 0.424 | 1.2226 | 1.6466 | 259.63 | -259.63
[6 empty] | 59 | 291.61 | 0.01737 | 7.289 | 260.96 | 916.3 | 1177.26 | 0.4255 | 1.2197 | 1.6452 | 260.77 | -260.77
[6 empty] | 60 | 292.71 | 0.01738 | 7.175 | 262.09 | 915.5 | 1177.59 | 0.427 | 1.2168 | 1.6438 | 261.9 | -261.9
[6 empty] | 61 | 293.79 | 0.01739 | 7.064 | 263.2 | 914.7 | 1177.9 | 0.4285 | 1.214 | 1.6425 | 263 | -263
[6 empty] | 62 | 294.85 | 0.0174 | 6.957 | 264.3 | 913.9 | 1178.2 | 0.43 | 1.2112 | 1.6412 | 264.1 | -264.1
[6 empty] | 63 | 295.9 | 0.01741 | 6.853 | 265.38 | 913.1 | 1178.48 | 0.4314 | 1.2085 | 1.6399 | 265.18 | -265.18
[6 empty] | 64 | 296.94 | 0.01742 | 6.752 | 266.45 | 912.3 | 1178.75 | 0.4328 | 1.2059 | 1.6387 | 266.24 | -266.24
[6 empty] | 65 | 297.97 | 0.01743 | 6.655 | 267.5 | 911.6 | 1179.1 | 0.4342 | 1.2032 | 1.6374 | 267.29 | -267.29
[6 empty] | 66 | 298.99 | 0.01744 | 6.56 | 268.55 | 910.8 | 1179.35 | 0.4356 | 1.2006 | 1.6362 | 268.34 | -268.34
[6 empty] | 67 | 299.99 | 0.01745 | 6.468 | 269.58 | 910.1 | 1179.68 | 0.4369 | 1.1981 | 1.635 | 269.36 | -269.36
[6 empty] | 68 | 300.98 | 0.01746 | 6.378 | 270.6 | 909.4 | 1180 | 0.4383 | 1.1955 | 1.6338 | 270.38 | -270.38
[6 empty] | 69 | 301.96 | 0.01747 | 6.291 | 271.61 | 908.7 | 1180.31 | 0.4396 | 1.193 | 1.6326 | 271.39 | -271.39
[6 empty] | 70 | 302.92 | 0.01748 | 6.206 | 272.61 | 907.9 | 1180.51 | 0.4409 | 1.1906 | 1.6315 |  | 0
[6 empty] | 71 | 303.88 | 0.01749 | 6.124 | 273.6 | 907.2 | 1180.8 | 0.4422 | 1.1881 | 1.6303 |  | 0
[6 empty] | 72 | 304.83 | 0.0175 | 6.044 | 274.57 | 906.5 | 1181.07 | 0.4435 | 1.1857 | 1.6292 |  | 0
[6 empty] | 73 | 305.76 | 0.01751 | 5.966 | 275.54 | 905.8 | 1181.34 | 0.4447 | 1.1834 | 1.6281 |  | 0
[6 empty] | 74 | 306.68 | 0.01752 | 5.89 | 276.49 | 905.1 | 1181.59 | 0.446 | 1.181 | 1.627 |  | 0
[6 empty] | 75 | 307.6 | 0.01753 | 5.816 | 277.43 | 904.5 | 1181.93 | 0.4472 | 1.1787 | 1.6259 |  | 0
[6 empty] | 76 | 308.5 | 0.01754 | 5.743 | 278.37 | 903.7 | 1182.07 | 0.4484 | 1.1764 | 1.6248 |  | 0
[6 empty] | 77 | 309.4 | 0.01754 | 5.673 | 279.3 | 903.1 | 1182.4 | 0.4496 | 1.1742 | 1.6238 |  | 0
[6 empty] | 78 | 310.29 | 0.01755 | 5.604 | 280.21 | 902.4 | 1182.61 | 0.4508 | 1.172 | 1.6228 |  | 0
[6 empty] | 79 | 311.16 | 0.01756 | 5.537 | 281.12 | 901.7 | 1182.82 | 0.452 | 1.1698 | 1.6218 |  | 0
[6 empty] | 80 | 312.03 | 0.01757 | 5.472 | 282.02 | 901.1 | 1183.12 | 0.4531 | 1.1676 | 1.6207 |  | 0
[6 empty] | 81 | 312.89 | 0.01758 | 5.408 | 282.91 | 900.4 | 1183.31 | 0.4543 | 1.1654 | 1.6197 |  | 0
[6 empty] | 82 | 313.74 | 0.01759 | 5.346 | 283.79 | 899.7 | 1183.49 | 0.4554 | 1.1633 | 1.6187 |  | 0
[6 empty] | 83 | 314.59 | 0.0176 | 5.285 | 284.66 | 899.1 | 1183.76 | 0.4565 | 1.1612 | 1.6177 |  | 0
[6 empty] | 84 | 315.42 | 0.01761 | 5.226 | 285.53 | 898.5 | 1184.03 | 0.4576 | 1.1592 | 1.6168 |  | 0
[6 empty] | 85 | 316.25 | 0.01761 | 5.168 | 286.39 | 897.8 | 1184.19 | 0.4587 | 1.1571 | 1.6158 |  | 0
[6 empty] | 86 | 317.07 | 0.01762 | 5.111 | 287.24 | 897.2 | 1184.44 | 0.4598 | 1.1551 | 1.6149 |  | 0
[6 empty] | 87 | 317.88 | 0.01763 | 5.055 | 288.08 | 896.5 | 1184.58 | 0.4609 | 1.153 | 1.6139 |  | 0
[6 empty] | 88 | 318.68 | 0.01764 | 5.001 | 288.91 | 895.9 | 1184.81 | 0.462 | 1.151 | 1.613 |  | 0
[6 empty] | 89 | 319.48 | 0.01765 | 4.948 | 289.74 | 895.3 | 1185.04 | 0.463 | 1.1491 | 1.6121 |  | 0
[6 empty] | 90 | 320.27 | 0.01766 | 4.896 | 290.56 | 894.7 | 1185.26 | 0.4641 | 1.1471 | 1.6112 |  | 0
[6 empty] | 91 | 321.06 | 0.01767 | 4.845 | 291.38 | 894.1 | 1185.48 | 0.4651 | 1.1452 | 1.6103 |  | 0
[6 empty] | 92 | 321.83 | 0.01768 | 4.796 | 292.18 | 893.5 | 1185.68 | 0.4661 | 1.1433 | 1.6094 |  | 0
[6 empty] | 93 | 322.6 | 0.01768 | 4.747 | 292.98 | 892.9 | 1185.88 | 0.4672 | 1.1413 | 1.6085 |  | 0
[6 empty] | 94 | 323.36 | 0.01769 | 4.699 | 293.78 | 892.3 | 1186.08 | 0.4682 | 1.1394 | 1.6076 |  | 0
[6 empty] | 95 | 324.12 | 0.0177 | 4.652 | 294.56 | 891.7 | 1186.26 | 0.4692 | 1.1376 | 1.6068 |  | 0
[6 empty] | 96 | 324.87 | 0.01771 | 4.606 | 295.34 | 891.1 | 1186.44 | 0.4702 | 1.1358 | 1.606 |  | 0
[6 empty] | 97 | 325.61 | 0.01772 | 4.561 | 296.12 | 890.5 | 1186.62 | 0.4711 | 1.134 | 1.6051 |  | 0
[6 empty] | 98 | 326.35 | 0.01772 | 4.517 | 296.89 | 889.9 | 1186.79 | 0.4721 | 1.1322 | 1.6043 |  | 0
[6 empty] | 99 | 327.08 | 0.01773 | 4.474 | 297.65 | 889.4 | 1187.05 | 0.4731 | 1.1304 | 1.6035 |  | 0
[6 empty] | 100 | 327.81 | 0.01774 | 4.432 | 298.4 | 888.8 | 1187.2 | 0.474 | 1.1286 | 1.6026 |  | 0
[6 empty] | 101 | 328.53 | 0.01775 | 4.391 | 299.15 | 888.2 | 1187.35 | 0.475 | 1.1268 | 1.6018 |  | 0
[6 empty] | 102 | 329.25 | 0.01775 | 4.35 | 299.9 | 887.6 | 1187.5 | 0.4759 | 1.1251 | 1.601 |  | 0
[6 empty] | 103 | 329.96 | 0.01776 | 4.31 | 300.64 | 887.1 | 1187.74 | 0.4768 | 1.1234 | 1.6002 |  | 0
[6 empty] | 104 | 330.66 | 0.01777 | 4.271 | 301.37 | 886.5 | 1187.87 | 0.4778 | 1.1216 | 1.5994 |  | 0
[6 empty] | 105 | 331.36 | 0.01778 | 4.232 | 302.1 | 886 | 1188.1 | 0.4787 | 1.1199 | 1.5986 |  | 0
[6 empty] | 106 | 332.05 | 0.01778 | 4.194 | 302.82 | 885.4 | 1188.22 | 0.4796 | 1.1182 | 1.5978 |  | 0
[6 empty] | 107 | 332.74 | 0.01779 | 4.157 | 303.54 | 884.9 | 1188.44 | 0.4805 | 1.1166 | 1.5971 |  | 0
[6 empty] | 108 | 333.42 | 0.0178 | 4.12 | 304.26 | 884.3 | 1188.56 | 0.4814 | 1.1149 | 1.5963 |  | 0
[6 empty] | 109 | 334.1 | 0.01781 | 4.084 | 304.97 | 883.7 | 1188.67 | 0.4823 | 1.1133 | 1.5956 |  | 0
[6 empty] | 110 | 334.77 | 0.01782 | 4.049 | 305.66 | 883.2 | 1188.86 | 0.4832 | 1.1117 | 1.5949 |  | 0
[6 empty] | 111 | 335.44 | 0.01782 | 4.015 | 306.37 | 882.6 | 1188.97 | 0.484 | 1.1101 | 1.5941 |  | 0
[6 empty] | 112 | 336.11 | 0.01783 | 3.981 | 307.06 | 882.1 | 1189.16 | 0.4849 | 1.1085 | 1.5934 |  | 0
[6 empty] | 113 | 336.77 | 0.01784 | 3.947 | 307.75 | 881.6 | 1189.35 | 0.4858 | 1.1069 | 1.5927 |  | 0
[6 empty] | 114 | 337.42 | 0.01784 | 3.914 | 308.43 | 881.1 | 1189.53 | 0.4866 | 1.1053 | 1.5919 |  | 0
[6 empty] | 115 | 338.07 | 0.01785 | 3.882 | 309.11 | 880.6 | 1189.71 | 0.4875 | 1.1037 | 1.5912 |  | 0
[6 empty] | 116 | 338.72 | 0.01786 | 3.85 | 309.79 | 880 | 1189.79 | 0.4883 | 1.1022 | 1.5905 |  | 0
[6 empty] | 117 | 339.36 | 0.01787 | 3.819 | 310.46 | 879.5 | 1189.96 | 0.4891 | 1.1007 | 1.5898 |  | 0
[6 empty] | 118 | 339.99 | 0.01787 | 3.788 | 311.12 | 879 | 1190.12 | 0.49 | 1.0992 | 1.5892 |  | 0
[6 empty] | 119 | 340.42 | 0.01788 | 3.758 | 311.78 | 878.4 | 1190.18 | 0.4908 | 1.0977 | 1.5885 |  | 0
[6 empty] | 120 | 341.25 | 0.01789 | 3.728 | 312.44 | 877.9 | 1190.34 | 0.4916 | 1.0962 | 1.5878 |  | 0
[6 empty] | 121 | 341.88 | 0.0179 | 3.699 | 313.1 | 877.4 | 1190.5 | 0.4924 | 1.0947 | 1.5871 |  | 0
[6 empty] | 122 | 342.5 | 0.01791 | 3.67 | 313.75 | 876.9 | 1190.65 | 0.4932 | 1.0933 | 1.5865 |  | 0
[6 empty] | 123 | 343.11 | 0.01791 | 3.642 | 314.4 | 876.4 | 1190.8 | 0.494 | 1.0918 | 1.5858 |  | 0
[6 empty] | 124 | 343.72 | 0.01792 | 3.614 | 315.04 | 875.9 | 1190.94 | 0.4948 | 1.0903 | 1.5851 |  | 0
[6 empty] | 125 | 344.33 | 0.01792 | 3.587 | 315.68 | 875.4 | 1191.08 | 0.4956 | 1.0888 | 1.5844 |  | 0
[6 empty] | 126 | 344.94 | 0.01793 | 3.56 | 316.31 | 874.9 | 1191.21 | 0.4964 | 1.0874 | 1.5838 |  | 0
[6 empty] | 127 | 345.54 | 0.01794 | 3.533 | 316.94 | 874.4 | 1191.34 | 0.4972 | 1.0859 | 1.5831 |  | 0
[6 empty] | 128 | 346.13 | 0.01794 | 3.507 | 317.57 | 873.9 | 1191.47 | 0.498 | 1.0845 | 1.5825 |  | 0
[6 empty] | 129 | 346.73 | 0.01795 | 3.481 | 318.19 | 873.4 | 1191.59 | 0.4987 | 1.0832 | 1.5819 |  | 0
[6 empty] | 130 | 347.32 | 0.01796 | 3.455 | 318.81 | 872.9 | 1191.71 | 0.4995 | 1.0817 | 1.5812 |  | 0
[6 empty] | 131 | 347.9 | 0.01797 | 3.43 | 319.43 | 872.5 | 1191.93 | 0.5002 | 1.0804 | 1.5806 |  | 0
[6 empty] | 132 | 348.48 | 0.01797 | 3.405 | 320.04 | 872 | 1192.04 | 0.501 | 1.079 | 1.58 |  | 0
[6 empty] | 133 | 349.06 | 0.01798 | 3.381 | 320.65 | 871.5 | 1192.15 | 0.5018 | 1.0776 | 1.5794 |  | 0
[6 empty] | 134 | 349.64 | 0.01799 | 3.357 | 321.25 | 871 | 1192.25 | 0.5025 | 1.0762 | 1.5787 |  | 0
[6 empty] | 135 | 350.21 | 0.018 | 3.333 | 321.85 | 870.6 | 1192.45 | 0.5032 | 1.0749 | 1.5781 |  | 0
[6 empty] | 136 | 350.78 | 0.018 | 3.31 | 322.45 | 870.1 | 1192.55 | 0.504 | 1.0735 | 1.5775 |  | 0
[6 empty] | 137 | 351.25 | 0.01801 | 3.287 | 323.05 | 869.6 | 1192.65 | 0.5047 | 1.0722 | 1.5769 |  | 0
[6 empty] | 138 | 351.91 | 0.01801 | 3.264 | 323.64 | 869.1 | 1192.74 | 0.5054 | 1.0709 | 1.5763 |  | 0
[6 empty] | 139 | 352.47 | 0.01802 | 3.242 | 324.23 | 868.7 | 1192.93 | 0.5061 | 1.0696 | 1.5757 |  | 0
[6 empty] | 140 | 353.02 | 0.01802 | 3.22 | 324.82 | 868.2 | 1193.02 | 0.5069 | 1.0682 | 1.5751 |  | 0
[6 empty] | 141 | 353.57 | 0.01803 | 3.198 | 325.4 | 867.7 | 1193.1 | 0.5076 | 1.0669 | 1.5745 |  | 0
[6 empty] | 142 | 354.12 | 0.01803 | 3.177 | 325.98 | 867.2 | 1193.18 | 0.5083 | 1.0657 | 1.574 |  | 0
[6 empty] | 143 | 354.67 | 0.01804 | 3.155 | 326.56 | 866.7 | 1193.26 | 0.509 | 1.0644 | 1.5734 |  | 0
[6 empty] | 144 | 355.21 | 0.01805 | 3.134 | 327.13 | 866.3 | 1193.43 | 0.5097 | 1.0631 | 1.5728 |  | 0
[6 empty] | 145 | 355.76 | 0.01806 | 3.114 | 327.7 | 865.8 | 1193.5 | 0.5104 | 1.0618 | 1.5722 |  | 0
[6 empty] | 146 | 356.29 | 0.01806 | 3.094 | 328.27 | 865.3 | 1193.57 | 0.5111 | 1.0605 | 1.5716 |  | 0
[6 empty] | 147 | 356.83 | 0.01807 | 3.074 | 328.83 | 864.9 | 1193.73 | 0.5118 | 1.0592 | 1.571 |  | 0
[6 empty] | 148 | 357.36 | 0.01808 | 3.054 | 329.39 | 864.5 | 1193.89 | 0.5124 | 1.058 | 1.5704 |  | 0
[6 empty] | 149 | 357.89 | 0.01808 | 3.034 | 329.95 | 864 | 1193.95 | 0.5131 | 1.0568 | 1.5699 |  | 0
[6 empty] | 150 | 358.42 | 0.01809 | 3.015 | 330.51 | 863.6 | 1194.11 | 0.5138 | 1.0556 | 1.5694 |  | 0
[6 empty] | 152 | 359.46 | 0.0181 | 2.977 | 331.61 | 862.7 | 1194.31 | 0.5151 | 1.0532 | 1.5683 |  | 0
[6 empty] | 154 | 360.49 | 0.01812 | 2.94 | 332.7 | 861.8 | 1194.5 | 0.5165 | 1.0507 | 1.5672 |  | 0
[6 empty] | 156 | 361.52 | 0.01813 | 2.904 | 333.79 | 860.9 | 1194.69 | 0.5178 | 1.0483 | 1.5661 |  | 0
[6 empty] | 158 | 362.53 | 0.01814 | 2.869 | 334.86 | 860 | 1194.86 | 0.5191 | 1.0459 | 1.565 |  | 0
[6 empty] | 160 | 363.53 | 0.01815 | 2.834 | 335.93 | 859.2 | 1195.13 | 0.5204 | 1.0436 | 1.564 |  | 0
[6 empty] | 162 | 364.53 | 0.01817 | 2.801 | 336.98 | 858.3 | 1195.28 | 0.5216 | 1.0414 | 1.563 |  | 0
[6 empty] | 164 | 365.51 | 0.01818 | 2.768 | 338.02 | 857.5 | 1195.52 | 0.5229 | 1.0391 | 1.562 |  | 0
[6 empty] | 166 | 366.48 | 0.01819 | 2.736 | 339.05 | 856.6 | 1195.65 | 0.5241 | 1.0369 | 1.561 |  | 0
[6 empty] | 168 | 367.45 | 0.0182 | 2.705 | 340.07 | 855.7 | 1195.77 | 0.5254 | 1.0346 | 1.56 |  | 0
[6 empty] | 170 | 368.41 | 0.01822 | 2.675 | 341.09 | 854.9 | 1195.99 | 0.5266 | 1.0324 | 1.559 |  | 0
[6 empty] | 172 | 369.35 | 0.01823 | 2.645 | 342.1 | 854.1 | 1196.2 | 0.5278 | 1.0302 | 1.558 |  | 0
[6 empty] | 174 | 370.29 | 0.01824 | 2.616 | 343.1 | 853.3 | 1196.4 | 0.529 | 1.028 | 1.557 |  | 0
[6 empty] | 176 | 371.22 | 0.01825 | 2.587 | 344.09 | 852.4 | 1196.49 | 0.5302 | 1.0259 | 1.5561 |  | 0
[6 empty] | 178 | 372.14 | 0.01826 | 2.559 | 345.06 | 851.6 | 1196.66 | 0.5313 | 1.0238 | 1.5551 |  | 0
[6 empty] | 180 | 373.06 | 0.01827 | 2.532 | 346.03 | 850.8 | 1196.83 | 0.5325 | 1.0217 | 1.5542 |  | 0
[6 empty] | 182 | 373.96 | 0.01829 | 2.505 | 347 | 850 | 1197 | 0.5336 | 1.0196 | 1.5532 |  | 0
[6 empty] | 184 | 374.86 | 0.0183 | 2.479 | 347.96 | 849.2 | 1197.16 | 0.5348 | 1.0175 | 1.5523 |  | 0
[6 empty] | 186 | 375.75 | 0.01831 | 2.454 | 348.92 | 848.4 | 1197.32 | 0.5359 | 1.0155 | 1.5514 |  | 0
[6 empty] | 188 | 376.64 | 0.1832 | 2.429 | 349.86 | 847.6 | 1197.46 | 0.537 | 1.0136 | 1.5506 |  | 0
[6 empty] | 190 | 377.51 | 0.01833 | 2.404 | 350.79 | 846.8 | 1197.59 | 0.5381 | 1.0116 | 1.5497 |  | 0
[6 empty] | 192 | 378.38 | 0.01834 | 2.38 | 351.72 | 846.1 | 1197.82 | 0.5392 | 1.0096 | 1.5488 |  | 0
[6 empty] | 194 | 379.24 | 0.01835 | 2.356 | 352.64 | 845.3 | 1197.94 | 0.5403 | 1.0076 | 1.5479 |  | 0
[6 empty] | 196 | 380.1 | 0.01836 | 2.333 | 353.55 | 844.5 | 1198.05 | 0.5414 | 1.0056 | 1.547 |  | 0
[6 empty] | 198 | 380.95 | 0.01838 | 2.31 | 354.46 | 843.7 | 1198.16 | 0.5425 | 1.0037 | 1.5462 |  | 0
[6 empty] | 200 | 381.79 | 0.01839 | 2.288 | 355.36 | 843 | 1198.36 | 0.5435 | 1.0018 | 1.5453 |  | 0
[6 empty] | 205 | 383.86 | 0.01842 | 2.234 | 357.58 | 841.1 | 1198.68 | 0.5461 | 0.9971 | 1.5432 |  | 0
[6 empty] | 210 | 385.9 | 0.01844 | 2.183 | 359.77 | 839.2 | 1198.97 | 0.5487 | 0.9925 | 1.5412 |  | 0
[6 empty] | 215 | 387.89 | 0.01847 | 2.134 | 361.91 | 837.4 | 1199.31 | 0.5512 | 0.988 | 1.5392 |  | 0
[6 empty] | 220 | 389.86 | 0.0185 | 2.087 | 364.02 | 835.6 | 1199.62 | 0.5537 | 0.9835 | 1.5372 |  | 0
[6 empty] | 225 | 391.79 | 0.01852 | 2.0422 | 366.09 | 833.8 | 1199.89 | 0.5561 | 0.9792 | 1.5353 |  | 0
[6 empty] | 230 | 393.68 | 0.01854 | 1.9992 | 368.13 | 832 | 1200.13 | 0.5585 | 0.975 | 1.5335 |  | 0
[6 empty] | 235 | 395.54 | 0.01857 | 1.9579 | 370.14 | 830.3 | 1200.44 | 0.5608 | 0.9708 | 1.5316 |  | 0
[6 empty] | 240 | 397.37 | 0.0186 | 1.9183 | 372.12 | 828.5 | 1200.62 | 0.5631 | 0.9667 | 1.5298 |  | 0
[6 empty] | 245 | 399.18 | 0.01863 | 1.8803 | 374.08 | 826.8 | 1200.88 | 0.5653 | 0.9627 | 1.528 |  | 0
[6 empty] | 250 | 400.95 | 0.01865 | 1.8438 | 376 | 825.1 | 1201.1 | 0.5675 | 0.9588 | 1.5263 |  | 0
[6 empty] | 255 | 402.7 | 0.01868 | 1.8086 | 377.89 | 823.4 | 1201.29 | 0.5697 | 0.9549 | 1.5246 |  | 0
[6 empty] | 260 | 404.42 | 0.0187 | 1.7748 | 379.76 | 821.8 | 1201.56 | 0.5719 | 0.951 | 1.5229 |  | 0
[6 empty] | 265 | 406.11 | 0.01873 | 1.7422 | 381.6 | 820.1 | 1201.7 | 0.574 | 0.9472 | 1.5212 |  | 0
[6 empty] | 270 | 407.78 | 0.01875 | 1.7107 | 383.42 | 818.5 | 1201.92 | 0.576 | 0.9436 | 1.5196 |  | 0
[6 empty] | 275 | 409.43 | 0.01878 | 1.6804 | 385.21 | 816.9 | 1202.11 | 0.5781 | 0.9399 | 1.518 |  | 0
[6 empty] | 280 | 411.05 | 0.0188 | 1.6511 | 386.98 | 815.3 | 1202.28 | 0.5801 | 0.9363 | 1.5164 |  | 0
[6 empty] | 285 | 412.65 | 0.01883 | 1.6288 | 388.73 | 813.7 | 1202.43 | 0.5821 | 0.9327 | 1.5148 |  | 0
[6 empty] | 290 | 414.23 | 0.01885 | 1.594 | 390.46 | 812.1 | 1202.56 | 0.5841 | 0.9292 | 1.5133 |  | 0
[6 empty] | 295 | 415.79 | 0.01887 | 1.5689 | 392.16 | 810.5 | 1202.66 | 0.586 | 0.9258 | 1.5118 |  | 0
[6 empty] | 300 | 417.33 | 0.0189 | 1.5433 | 393.84 | 809 | 1202.84 | 0.5879 | 0.9225 | 1.5104 |  | 0
[6 empty] | 310 | 420.35 | 0.01894 | 1.4944 | 397.15 | 806 | 1203.15 | 0.5916 | 0.9159 | 1.5075 |  | 0
[6 empty] | 320 | 423.29 | 0.01899 | 1.4485 | 400.39 | 803 | 1203.39 | 0.5952 | 0.9094 | 1.5046 |  | 0
[6 empty] | 330 | 426.16 | 0.01904 | 1.4053 | 403.56 | 800 | 1203.56 | 0.5988 | 0.9031 | 1.5019 |  | 0
[6 empty] | 340 | 428.97 | 0.01908 | 1.3645 | 406.66 | 797.1 | 1203.76 | 0.6022 | 0.897 | 1.4992 |  | 0
[6 empty] | 350 | 431.72 | 0.01913 | 1.326 | 409.69 | 794.2 | 1203.89 | 0.6056 | 0.891 | 1.4966 |  | 0
[6 empty] | 360 | 434.4 | 0.01917 | 1.2895 | 412.67 | 791.4 | 1204.07 | 0.609 | 0.8851 | 1.4941 |  | 0
[6 empty] | 370 | 437.03 | 0.01921 | 1.255 | 415.59 | 788.6 | 1204.19 | 0.6122 | 0.8794 | 1.4916 |  | 0
[6 empty] | 380 | 439.6 | 0.01925 | 1.2222 | 418.45 | 785.8 | 1204.25 | 0.6153 | 0.8738 | 1.4891 |  | 0
[6 empty] | 390 | 442.12 | 0.0193 | 1.191 | 421.27 | 783.1 | 1204.37 | 0.6184 | 0.8633 | 1.4817 |  | 0
[6 empty] | 400 | 444.59 | 0.0193 | 1.1613 | 424 | 780.5 | 1204.5 | 0.6214 | 0.863 | 1.4844 |  | 0
[6 empty] | 410 | 447.01 | 0.0194 | 1.133 | 426.8 | 777.7 | 1204.5 | 0.6243 | 0.8578 | 1.4821 |  | 0
[6 empty] | 420 | 449.39 | 0.0194 | 1.1061 | 429.4 | 775.2 | 1204.6 | 0.6272 | 0.8527 | 1.4799 |  | 0
[6 empty] | 430 | 451.73 | 0.0194 | 1.0803 | 432.1 | 772.5 | 1204.6 | 0.6301 | 0.8476 | 1.4777 |  | 0
[6 empty] | 440 | 454.02 | 0.0195 | 1.0556 | 434.6 | 770 | 1204.6 | 0.6329 | 0.8426 | 1.4755 |  | 0
[6 empty] | 450 | 456.28 | 0.0195 | 1.032 | 437.2 | 767.4 | 1204.6 | 0.6356 | 0.8378 | 1.4734 |  | 0
[6 empty] | 460 | 458.5 | 0.0196 | 1.0094 | 439.7 | 764.9 | 1204.6 | 0.6383 | 0.833 | 1.4713 |  | 0
[6 empty] | 470 | 460.68 | 0.0196 | 0.9878 | 442.2 | 762.4 | 1204.6 | 0.641 | 0.8283 | 1.4693 |  | 0
[6 empty] | 480 | 462.82 | 0.0197 | 0.967 | 444.6 | 759.9 | 1204.5 | 0.6436 | 0.8237 | 1.4673 |  | 0
[6 empty] | 490 | 464.93 | 0.0197 | 0.947 | 447 | 757.5 | 1204.5 | 0.6462 | 0.8191 | 1.4653 |  | 0
[6 empty] | 500 | 467.01 | 0.0197 | 0.9278 | 449.4 | 755 | 1204.4 | 0.6487 | 0.8147 | 1.4634 |  | 0
[6 empty] | 520 | 471.07 | 0.0198 | 0.8915 | 454.1 | 750.1 | 1204.2 | 0.6536 | 0.806 | 1.4596 |  | 0
[6 empty] | 540 | 475.01 | 0.0199 | 0.8578 | 458.6 | 745.4 | 1204 | 0.6584 | 0.7976 | 1.456 |  | 0
[6 empty] | 560 | 478.85 | 0.02 | 0.8265 | 463 | 740.8 | 1203.8 | 0.6631 | 0.7893 | 1.4524 |  | 0
[6 empty] | 580 | 482.58 | 0.0201 | 0.7973 | 467.4 | 736.1 | 1203.5 | 0.6676 | 0.7813 | 1.4489 |  | 0
[6 empty] | 600 | 486.21 | 0.0201 | 0.7698 | 471.6 | 731.6 | 1203.2 | 0.672 | 0.7734 | 1.4454 |  | 0
[6 empty] | 620 | 489.75 | 0.0202 | 0.744 | 475.7 | 727.2 | 1202.9 | 0.6763 | 0.7658 | 1.4421 |  | 0
[6 empty] | 640 | 493.21 | 0.0203 | 0.7198 | 479.8 | 722.7 | 1202.5 | 0.6805 | 0.7584 | 1.4389 |  | 0
[6 empty] | 660 | 496.58 | 0.0204 | 0.6971 | 483.8 | 718.3 | 1202.1 | 0.6846 | 0.7512 | 1.4358 |  | 0
[6 empty] | 680 | 499.88 | 0.0204 | 0.6757 | 487.7 | 714 | 1201.7 | 0.6886 | 0.7441 | 1.4327 |  | 0
[6 empty] | 700 | 503.1 | 0.0205 | 0.6554 | 491.5 | 709.7 | 1201.2 | 0.6925 | 0.7371 | 1.4296 |  | 0
[6 empty] | 720 | 506.25 | 0.0206 | 0.6362 | 495.3 | 705.4 | 1200.7 | 0.6963 | 0.7303 | 1.4266 |  | 0
[6 empty] | 740 | 509.34 | 0.0207 | 0.618 | 499 | 701.2 | 1200.2 | 0.7001 | 0.7237 | 1.4238 |  | 0
[6 empty] | 760 | 512.36 | 0.0207 | 0.6007 | 502.6 | 697.1 | 1199.7 | 0.7037 | 0.7172 | 1.4209 |  | 0
[6 empty] | 780 | 515.33 | 0.0208 | 0.5843 | 506.2 | 692.9 | 1199.1 | 0.7073 | 0.7108 | 1.4181 |  | 0
[6 empty] | 800 | 518.23 | 0.0209 | 0.5687 | 509.7 | 688.9 | 1198.6 | 0.7108 | 0.7045 | 1.4153 |  | 0
[6 empty] | 820 | 521.08 | 0.0209 | 0.5538 | 513.2 | 684.8 | 1198 | 0.7143 | 0.6983 | 1.4126 |  | 0
[6 empty] | 840 | 523.88 | 0.021 | 0.5396 | 516.6 | 680.8 | 1197.4 | 0.7177 | 0.6922 | 1.4099 |  | 0
[6 empty] | 860 | 526.63 | 0.0211 | 0.526 | 520 | 676.8 | 1196.8 | 0.721 | 0.6862 | 1.4072 |  | 0
[6 empty] | 880 | 529.33 | 0.0212 | 0.513 | 523.3 | 672.8 | 1196.1 | 0.7243 | 0.6803 | 1.4046 |  | 0
[6 empty] | 900 | 531.98 | 0.0212 | 0.5006 | 526.6 | 668.8 | 1195.4 | 0.7275 | 0.6744 | 1.4019 |  | 0
[6 empty] | 920 | 534.59 | 0.0213 | 0.4886 | 529.8 | 664.9 | 1194.7 | 0.7307 | 0.6687 | 1.3994 |  | 0
[6 empty] | 940 | 537.16 | 0.0214 | 0.4772 | 533 | 661 | 1194 | 0.7339 | 0.6631 | 1.397 |  | 0
[6 empty] | 960 | 539.68 | 0.0214 | 0.4663 | 536.2 | 657.1 | 1193.3 | 0.737 | 0.6576 | 1.3946 |  | 0
[6 empty] | 980 | 542.17 | 0.0215 | 0.4557 | 539.3 | 653.3 | 1192.6 | 0.74 | 0.6521 | 1.3921 |  | 0
[6 empty] | 1000 | 544.61 | 0.0216 | 0.4456 | 542.4 | 649.4 | 1191.8 | 0.743 | 0.6467 | 1.3897 |  | 0