The feed system shall be a Bryan Model  HFS - ____________ horizontal type boiler feed system, with a tank size of _____ (50 to 500) gallons design to operate at _____ PSI boiler relief valve setting with a total boiler capacity of _____ lbs/Hr or _____ boiler HP.

BOILER FEED SYSTEM:

- The boiler feed system shall have the storage capacity to overflow of at least 1 gallon per 1 boiler horsepower of the boiler(s) it is servicing.  The boiler feed pumps shall be supplied with the boiler feed system and be capable of pumping twice the evaporation rate of the boiler at 3% above the boiler relief valve setting per the ASME code.  The boiler and the boiler feed system shall be supplied by the same manufacturer to obtain single source responsibility.

- The storage tank shell and heads shall be constructed of ¼” thick minimum carbon steel to the specifications of SA516 Grade 70 or SA53B and shall be capable of holding the specified gallons to overflow.  The horizontal vessel will be supplied (at a minimum) with 3” threaded connections for condensate return and vent, pump suction coupling of adequate size, a manual fill connection, overflow connection, drain connection, a sight glass with brass valves installed, and a blowout opening properly designed to keep the pressure in the tank at atmospheric conditions.  All exposed metal surfaces shall be protected with a suitable heat and rust resisting paint.  The base shall extend in front of the storage vessel for pump mounting and easier access to the pump(s) for inspection and maintenance.

- The boiler feed system is to be fully trimmed by the manufacturer including the following items:

  - Make-Up Water Assembly: A mechanical float-type make-up water control shall be provided to accept incoming water up to a differential pressure of 100 psi.  The make-up valve assembly shall mount directly into the tank to eliminate unnecessary external piping and be removable from the outside of the vessel for easy maintenance and inspection.  The make-up valve shall be made of brass or bronze with a copper float that does not require external power for operation.

  - Misc. Gauges: A temperature gauge shall be supplied and installed by the manufacturer.  The gauge shall be sized suitable for the operation and design range of the boiler feed system.  A gauge glass shall be supplied and installed to indicate the water level in the tank.  The gauge glass shall be protected from objects by metal protectors and have shut off valves on both ends.

- The boiler feed system shall be supplied from the manufacture with a pump package which shall include the following:

  - Stand:  The storage tank shall be supported by two saddles that are attached to four legs made of 2” standard diameter pipe to supply enough net positive suction head required for the pumps plus additional safety factor to avoid cavitation.  The unit and pumps shall be mounted on a 4” channel structural steel base with a minimum ¼” thk. steel plate floor with proper support and braces.  All exposed metal surfaces shall be protected with a suitable heat and rust resisting paint.  The base shall extend in front of the storage vessel for pump mounting and easier access to the pump(s) for inspection and maintenance.

  - Pump(s):  Pump size shall be based on pump schedule and be able to pump into the boiler at least 3% above the boiler relief valve setting to satisfy the ASME code.  The pump shall be a vertical multistage pump (Goulds SSV,  Grundfos CR, or similar)  with stainless steel impellers and a minimum of 250F seals.  The pump motors shall be 3-phase, TEFC motors.

  - Pump Mounting and Piping:  The pump(s) shall be mounted to the base.  The pump suction piping shall include a gate valve, strainer, and flexible connector for each pump.  Pump discharge piping shall include a liquid filled pressure gauge with shut-off valve and pump throttling valve.  Suction and discharge piping shall be sized based on a maximum velocity of 4 ft/sec of rated flow.  All suction and discharge components will be factory installed.

  - Pump Electrical Components:  The pump(s) shall be supplied with a TEFC motor.  Each pump circuit shall have a NEMA # 12 IEC enclosed motor starter with overloads.  Also included is a hand-off-auto switch  for each pump.  All pump

electrical components shall be completely

factory wired.