The deaerator shall be a Bryan Model _____ vertical tray type feedwater deaerator, with a capacity of _____ lbs/Hr or _____ boiler HP.

DEAERATOR:

- The deaerator capacity rating shall exceed the capacity of the steam system it is servicing and have a minimum of 10 minutes storage capacity to the overflow.  The deaerator shall be designed for oxygen removal to 0.005 cc/l  (7 ppb) or less and carbon dioxide removal to a zero measurable level in the effluent throughout all load conditions between 0% and 100% of rated capacity.  The deaeration process will take place in a 5-15 psig steam environment that will heat the water to 228-250F requiring a pressurized vessel.  The deaerator shall be manufactured in strict accordance with the ASME Section VIII, Div. 1 code and bare the ASME stamp for a maximum working pressure of 50 psig at 300F.  An atmospheric deaerator is not acceptable.  A minimum of 1/16” corrosion allowance shall be added to the ASME calculated material thickness for heads and shell and will be noted on the ASME data report (form U-1).  The deaerator vessel will be built and designed by the same manufacturer.  The company supplying the deaerator and the manufacturer listed on the certified papers (known as the ASME data report form U-1) will be the same company or corporation  in order to have one company responsible for the entire unit and to eliminate subcontracting of the pressure vessel  This must be proven at the time of installation and before the final release of payment for the unit.

- The deaerator is to be of the tray type design.  Flow of steam shall be such that the steam entering the heater first comes in contact with the hottest water which is leaving the last row of trays and then proceeds upward through the tray stack in a counter-flow fashion.  The water to be deaerated will enter the vessel through a stainless steel spray tube.  The spray tube will disperse water into a 304L stainless steel box that is sealed so that escaping gasses cannot come in contact with the vessel walls. The gasses escape through a 304L vent condenser pipe on top of the tray box that extends out the top of the vessel.  The spray tube directs the water into sections of a 304L stainless steel vent condenser seal welded on top of the tray box.  The water falls downward from the vent condenser and spreads over the stainless steel trays and, after deaeration, falls into the storage area.  The stainless steel (304L) trays will be removable through a minimum 20” dia. hinged

tray access door.  Each tray shall  be of stamped and/or welded construction.  Rivets are not acceptable due to coming loose during years of service.   The deaerator will be designed so that undeaerated water will only come into contact with stainless steel components and corrosive gasses have no access to the pressure vessel heads or shell for longevity of the pressure vessel.  Spray type deaerators that require epoxy (or similar spray-on) lining to accomplish vessel protection is not permitted.

C.	The tray type deaerator is to be fully trimmed by the manufacturer including the following items:

- Low Level Control: An external float type control is to be supplied to monitor a low level condition.  A low level shall ring an alarm bell and light a red light on the control panel notifying the operator.  The control shall also shut off the boiler feed pumps protecting them from harm.

- High Level Control: An external float type control is to be supplied to monitor a high level condition.  A high level shall ring an alarm bell and light a red light on the control panel notifying the operator.  The high level control shall be activated before the water reaches the overflow level.

4.	Overflow Trap: A mechanical self-contained external float type overflow trap shall be supplied to overflow the water in the storage area before flooding the deaerator.  The overflow trap body is to be constructed of cast iron.  Inside the body, a stainless steel ball float automatically operates a double-seated brass valve.  The cast iron body is to be bolted together in order to take apart for inspection/maintenance of the valve assembly.  A butterfly valve is to be supplied between the deaerator and the trap for inspection without having to shut down the deaerator.

- Make-Up Water Assembly: An electric water level controller and make-up water valve is to be supplied to monitor the level of water storage in the deaerator and add make-up water when necessary for continued operation.  The level to activate

the water valve shall be field adjustable  within a 12” span to match desirable operating conditions without disturbing the piping or shutting down the deaerator.  The water valve will accept a 4-20 mA signal from the level controller for modulation and shall be suitable for operation with a pressure differential of up to 150 psi.  The valve will be shipped loose for field installation.

- Pressure Reducing Valve: A self-contained pilot operated valve shall be supplied to reduce the available steam pressure to the operating pressure of the deaerator (5-15 psig).  The valve is to be shipped loose for field installation.  Relief valve(s) accepted for ASME service shall also be supplied.  The relieving capacity of the valves shall be greater than the maximum capacity of the pressure reducing valve and set to relieve at the deaerator design pressure.

- Vacuum Breaker: A vacuum breaker is to be supplied to protect the deaerator vessel from a vacuum condition during operation.

- Vent Valve: A manual valve shall be supplied to vent the deaerator.  The valve is to have the ability to be field adjustable with a 1/8” drilled orifice to avoid complete shut off capability.

- Misc. Gauges: A pressure and temperature gauge shall be supplied and installed by the manufacturer.  The gauges shall be sized suitable for the operation and design range of the deaerator and follow any ASME or local codes and requirements.  A gauge glass shall be supplied and installed to cover the water level range from low level to overflow level.  The gauge glass shall be enclosed with a protective metal case to protect from getting hit by outside objects and be so mounted to protect from getting broken.

- Alarm Package:  The alarm package shall consist of a Nema 12 enclosure with alarm bell, alarm silencing switch, and high and low level red lights to indicate by sound and visually a high and low level alarm condition.

- The tray type deaerator shall be supplied from the manufacture with a pump package which shall include the following:

- Stand:  The stand shall be made of 4”x4”  (min.) tubing and be structurally sound and designed for the weight of the unit.  The stand shall be bolted to the deaerator in order for easy removal for installation and shipment.  All wiring shall be complete between the deaerator and stand before shipment and broken at terminals when

the stand is unbolted.  The stand height shall be governed by the net positive suction head required by the pumps but never less than 48” tall to assist in servicing the pumps.

- Pump(s):  Pump size shall be based on pump schedule and be able to pump into the boiler at least 3% above the boiler relief valve setting to satisfy the ASME code.  The pump shall be a vertical multistage pump (Armstrong VMS, Goulds SSV,  Grundfos CR, or similar)  with stainless steel impellers and a minimum of 250F seals.  The pump motors shall be 3-phase, TEFC motors.

- Pump Mounting and Piping:  The pump(s) shall be mounted to the base.  The pump suction piping shall include a vortex breaker, gate valve, strainer, and flexible connector for each pump.  Pump discharge piping shall include a liquid filled pressure gauge with shut-off valve and pump throttling valve.  Suction and discharge piping shall be sized based on a maximum velocity of 4 ft/sec of rated flow.  All suction and discharge components will be factory installed.  Piping may be taken apart at the unions or flanges for shipment.

4.	Pump Electrical Components:  The pump shall be supplied with a TEFC motor.  Each pump shall have a thru-the-door (3-phase) pump disconnect switch and 3-phase protection by Class LPJ fusing or similar fuse.  The pump shall also be protected from the following:  undervoltage, overvoltage, motor overload, ground fault, and phase to ground short.   Each pump will have its own variable frequency drive with pressure transducer and pressure controller.  The VFD will modulate the pump’s output based on a 4-20 mA signal from the transducer.  A pressure controller with display shall be provided for ease of start-up and setting the pump discharge to a desired pressure.   The circuit for each pump shall also be provided with the following digital displays:  Frequency (Hertz), Current (Amps), and Voltage (Volts).  An on/off switch and pilot light shall also be provided for each pump.  All pump electrical components shall be wired and factory checked before shipment.  A fused control circuit transformer shall also be provided to reduce the 3-phase supplied power to 120/1/60 for the control circuit.  The complete deaerator system will have single point electrical connection located in a UL listed Nema 12 control panel.  Liquid tight conduit shall be used between the panel and external electrical items mounted on the deaerator package.