The deaerator shall be a Bryan Model _____ low profile vertical tray type feedwater deaerator, with a capacity of _____ lbs/Hr or _____ boiler HP.

DEAERATOR:

- The deaerator capacity rating shall exceed the capacity of the steam system it is servicing and have a minimum of 10 minutes storage capacity to the overflow.  The deaerator shall be designed for oxygen removal to 0.005 cc/l  (7 ppb) or less and carbon dioxide removal to a zero measurable level in the effluent throughout all load conditions between 0% and 100% of rated capacity.  The deaeration process will take place in a 5-15 psig steam environment that will heat the water to 228-250F requiring a pressurized vessel. The deaerator is to be of the vertical design and be less than 18” from the floor to keep the over-all height of the unit to a minimum.  The deaerator shall be manufactured in strict accordance with the ASME Section VIII, Div. 1 code and bare the ASME stamp for a maximum working pressure of 50 psig at 300F.  An atmospheric deaerator is not acceptable.  A minimum of 1/16” corrosion allowance shall be added to the ASME calculated material thickness for heads and shell and will be noted on the ASME data report (form U-1).  The deaerator vessel will be built and designed by the same manufacturer.  The company supplying the deaerator and the manufacturer listed on the certified papers (known as the ASME data report form U-1) will be the same company or corporation  in order to have one company responsible for the entire unit and to eliminate subcontracting of the pressure vessel  This must be proven at the time of installation and before the final release of payment for the unit.

- The deaerator is to be of the tray type design.  Spray type deaerators are not acceptable.  Flow of steam shall be such that the steam entering the heater first comes in contact with the hottest water which is leaving the last row of trays and then proceeds upward through the tray stack in a counter-flow fashion.  The water to be deaerated will enter the vessel through a stainless steel spray tube.  The spray tube will disperse water into a 304L stainless steel box that is sealed so that escaping gasses can not come in contact with the vessel walls. The gasses escape through a 304L vent condenser pipe on top of the tray box that extends out the top of the vessel.  The spray tube directs the water into sections of a 304L stainless steel vent condenser seal welded on top of the tray box.  The water falls downward from the vent condenser and spreads over the stainless steel trays and, after deaeration, falls into the storage area.  The stainless steel (304L) trays will be removable through a minimum 20” dia. hinged tray access door.  Each tray shall weigh no more than 30lbs. for easy handling and inspection and shall be of welded construction.  Rivets are not acceptable.   The deaerator will be designed so that undeaerated water will only come into contact with stainless steel components.

- The tray type deaerator is to be fully trimmed by the manufacturer including the following items:

  - Low Level Control: An external float type control is to be supplied to monitor a low level condition.  A low level shall ring an alarm bell and light a red light on the control panel notifying the operator.  The control shall also shut off the deaerator pumps protecting them from harm.

  - High Level Control: An external float type control is to be supplied to monitor a high level condition.  A high level shall ring an alarm bell and light a red light on the control panel notifying the operator.  The high level control shall be activated before the water reaches the overflow level.

  - Overflow trap: A mechanical self-contained external float type overflow trap shall be supplied to overflow the water in the storage area before flooding the deaerator.  The overflow trap body is to be constructed of cast iron.  Inside the body, a stainless steel ball float automatically operates a double-seated brass valve.  The cast iron body is to be bolted together in order to take apart for inspection/maintenance of the valve assembly.  A butterfly valve is to be supplied between the deaerator and the trap for inspection without having to shut down the deaerator.

4.	Make-Up water assembly: An electric water level controller and make-up water valve is to be supplied to monitor the level of water storage in the deaerator and add make-up water when necessary for continued operation.  The level to activate the water valve shall be field adjustable to match desirable operating conditions.  The water valve shall be suitable for operation with a pressure differential of up to 150 psi.  The valve shall default to a closed position when de-energized and be a

modulating or slow closing valve in order to reduce or eliminate water hammer.  The valve shall be factory piped with a 3-valve bypass assembly and strainer.

- Pressure Reducing Valve: A self-contained pilot operated valve shall be supplied to reduce the available steam pressure to the operating pressure of the deaerator (5-15 psig).  The valve is to be shipped loose for field installation.  Relief valve(s) accepted for ASME service shall also be supplied.  The relieving capacity of the valves shall be greater than the maximum capacity of the pressure reducing valve and set to relieve at 50 psig.

- Vacuum Breaker: A vacuum breaker is to be supplied to release any vacuum in the deaerator during operation.

- Vent Valve: A manual valve shall be supplied to vent the deaerator.  The valve is to have the ability to be field adjustable with a 1/8” drilled orifice to avoid complete shut off capability.

- Drain Valve: A gate valve is to be supplied and sized the same diameter as the drain connection and be supplied by the manufacturer.

- Misc. Gauges: A pressure and temperature gauge shall be supplied and installed by the manufacturer.  The gauges shall be sized suitable for the operation and design range of the deaerator and follow any ASME or local codes and requirements.  A gauge glass shall be supplied and installed to cover the water level range from low level to overflow level.  The gauge glass shall be protected from getting hit by outside objects and be so mounted to protect from getting broken.

- Pump Suction: The pump suction connection shall be sized based on a velocity 4 ft/sec of twice the deaerator capacity.  A separate gate valve, strainer, and flexible connector shall be supplied for each pump.

D.	The tray type deaerator shall be supplied from the manufacture with a pump package which shall include the following:

- Pump Platform:  The pump platform shall be structurally sound and designed for the weight of the unit.  The platform shall not be greater than 6” off the floor and will encompass the entire deaerator package including the pumps.

- Pump(s):  Pump size shall be based on pump schedule and be able to pump into the boiler at least 3% above the boiler relief valve setting to satisfy the ASME code.  The pump shall be a Roth multistage feedwater pump.  Pump shall be capable of successful operation with 1 ft. NPSH.  Full required capacity shall be guaranteed at the specified temperature, at 1 ft. NPSH.  Motor speed shall not exceed 1750 RPM.  Pump shall be center mounted with permanently lubricated ball bearings and a stainless steel shaft.  The seal seat shall be silicon carbide for temperatures up to 250F.  The pump shall be fitted with iron liners and with 416SS impellers for temperatures up to 250F.  The pump motors shall be 3-phase, TEFC motors.

- Pump Mounting and Piping:  The pump(s) shall be mounted to the base.  The pump suction piping shall include a vortex breaker, gate valve, strainer, and flexible connector for each pump.  Pump discharge piping shall include a liquid filled pressure gauge with shut-off valve and pump throttling valve.  Suction and discharge piping shall be sized based on a maximum velocity of 4 ft/sec of rated flow.  All suction and discharge components will be factory installed.  Piping may be taken apart at the unions or flanges for shipment.

- Pump Electrical Components:  The pump shall be supplied with a TEFC motor.  Each pump shall have a thru-the-door (3-phase) pump disconnect switch,  3-phase protection by Class LPJ fusing or similar fuse, and a motor starter with overloads.   A hand-off-auto switch and pilot light shall also be provided for each pump.  All pump electrical components shall be wired and factory checked before shipment.  A fused control circuit transformer shall also be provided to reduce the 3-phase supplied power to 120/1/60 for the control circuit.  The complete deaerator system will have single point electrical connection located in a UL listed Nema 12 control panel.  Liquid tight conduit shall be used between the panel and external electrical items mounted on the deaerator package.